## R-CHE
LABORATORY WATER ANALYSIS - TEST SHEET | [6 empty] | Rev12 | LABORATORY WATER ANALYSIS REPORT | [6 empty] | Rev12
Dealer Name | [5 empty] | Sample No. | 20170714CHE01 | DEALER NAME | [5 empty] | Sample No. | 20170714CHE01
Reference Name | [5 empty] | Date Received |  | REFERENCE NAME | [5 empty] | Date Received | 0
Sample Type | [5 empty] | Date Tested |  | Sample Type | TBC |  |  |  |  | Date Reported | 2024-05-20
Test Parameter | Units / Name: | Result | DL | GV | MAV | Comment |  | Test Parameter | Units | Result | GV1 | MAV2 | Comments
pH | - | 7.3 |  | 7.0 - 8.5 | - |  |  | pH | - | 7.3 | 7.0 - 8.5 | - | Neutral
Alkalinity | mg/L CaCO3 | 40 | 5 | - | - |  |  | Alkalinity | mg/L CaCO3 | 40 | - | - | Low
Total Hardness | mg/L CaCO3 | 42 | 5 | ≤200 | - |  |  | Total Hardness | mg/L CaCO3 | 42 | ≤200 | - | Slightly Hard
Calcium Hardness | mg/L CaCO3 |  | 5 | - | - |  |  | Calcium Hardness | mg/L CaCO3 | <5 | - | - | Trace
Magnesium Hardness | mg/L CaCO3 | 42 | 5 | - | - |  |  | Magnesium Hardness | mg/L CaCO3 | 42 | - | - | Slightly Hard | Calculated Result
Free Carbon Dioxide | mg/L CO2 | 4.001 |  | - | - |  |  | Free Carbon Dioxide | mg/L CO2 | 4.001 | - | - | Low | Calculated Result
Langelier Saturation | - | -1.6 |  | - | - |  |  | Langelier Saturation Index | - | -1.6 | - | - | Corrosive | Calculated Result
Silica | mg/L SiO2 |  | 1 | - | - |  |  | Silica | mg/L SiO2 | <5 | - | - | Not Detected
Nitrate | mg/L NO3 |  | 1 | - | 50 |  |  | Nitrate | mg/L NO3 | <1 | - | 50 | Not Detected
Sulphate | mg/L SO4 |  | 1 | ≤250 |  |  |  | Sulphate | mg/L SO4 | <1 | ≤250 | - | Not Detected
Total Iron | mg/L |  | 0.01 | ≤0.3 | - |  |  | Total Iron | mg/L | <0.01 | ≤0.3 | - | Not Detected
Total Manganese | mg/L |  | 1.5 | ≤0.04 | 0.4 |  |  | Total Manganese | mg/L | <0.01 | ≤0.04 | 0.4 | Not Detected | <0.04 Staining, <0.10 Taste
Total Aluminium | mg/L |  | 0.01 | ≤0.1 | - |  |  | Total Aluminium | mg/L | <0.01 | ≤0.1 | - | Not Detected
Total Copper | mg/L |  | 0.01 | ≤1 | 2 |  |  | Total Copper | mg/L | <0.01 | ≤1 | 2 | Not Detected
Total Dissolved Solids | mg/L |  | 10 | ≤1000 | - |  |  | Total Dissolved Solids | mg/L | <10 | ≤1000 | - | Trace | Calculated Result
Chloride | mg/L |  | 1 | ≤250 | - |  |  | Chloride | mg/L | <1 | ≤250 | - | Trace
Sodium | mg/L |  |  | ≤200 | - |  |  | Sodium | mg/L | <1 | ≤200 | - | Trace
Conductivity | mS/m |  |  | - | - |  |  | Conductivity | mS/m | <5 | - | - | -
Conductivity | µS/cm |  |  | - | - |  |  | Conductivity | µS/cm | 0 | - | - | -
Turbidity | NTU |  | 0.05 | ≤5 | - |  |  | Turbidity | NTU | <0.05 | ≤5 | - | Very Low | ≤ 5 for Appearance
Colour | °H |  | 5 | - | - |  |  | Colour | °H | <5 | - | - | Very Low | ≤ 15 TCU for Appearance
UV254 Transmission | % T10 |  | 5 | - | - |  |  | UV254 Transmission | % T10 | <5 | - | - | Very Poor
Comments: | The sample was |  | clear |  | with | some significant sediments |  | Comments: The sample was clear with some significant sediments
LSI comment: | The negative LSI indicates corrosive water. | [6 empty] | The negative LSI indicates corrosive water.
Silica comment:
Iron comment:
Manganese comment:
Chloride comment:
MAV comment:
[8 empty] | GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
[8 empty] | MAV2 | Maximum Acceptable Value - Water Services (Drinking Water Standards for New Zealand) Regulations 2022
[8 empty] | mg/L | = ppm, = g/m3
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## R-SHO
LABORATORY WATER ANALYSIS - TEST SHEET | [6 empty] | Rev12 | LABORATORY WATER ANALYSIS REPORT | [6 empty] | Rev12
Dealer Name | [5 empty] | Sample No. | 20170714SHO01 | DEALER NAME | [5 empty] | Sample No. | 20170714SHO01
Reference Name | [5 empty] | Date Received |  | REFERENCE NAME | [5 empty] | Date Received | 0
Sample Type | [5 empty] | Date Tested |  | Sample Type | TBC |  |  |  |  | Date Reported | 2024-05-20
Test Parameter | Units / Name: |  | DL | GV | MAV | Comment |  | Test Parameter | Units | Result | GV1 | MAV2 | Comments
pH | - |  |  | 7.0 - 8.5 | - |  |  | pH | - | 0 | 7.0 - 8.5 | - | #N/A
Alkalinity | mg/L CaCO3 |  | 5 | - | - |  |  | Alkalinity | mg/L CaCO3 | <5 | - | - | Trace
Total Hardness | mg/L CaCO3 |  | 5 | ≤200 | - |  |  | Total Hardness | mg/L CaCO3 | <5 | ≤200 | - | Trace
Free Carbon Dioxide | mg/L CO2 | 9999999.9981 |  | - | - |  |  | Free Carbon Dioxide | mg/L CO2 | 9999999.9981 | - | - | Very High | Calculated Result
Langelier Saturation | - | -10.6 |  | - | - |  |  | Langelier Saturation Index | - | -10.6 | - | - | #N/A | Calculated Result
Silica | mg/L SiO2 |  | 1 | - | - |  |  | Silica | mg/L SiO2 | <5 | - | - | Not Detected
Total Iron | mg/L |  | 0.01 | ≤0.3 | - |  |  | Total Iron | mg/L | <0.01 | ≤0.3 | - | Not Detected
Total Manganese | mg/L |  | 1.5 | ≤0.04 | 0.4 |  |  | Total Manganese | mg/L | <0.01 | ≤0.04 | 0.4 | Not Detected | <0.04 Staining, <0.10 Taste
Total Dissolved Solids | mg/L |  | 10 | ≤1000 | - |  |  | Total Dissolved Solids | mg/L | <10 | ≤1000 | - | Trace | Calculated Result
UV254 Transmission | % T10 |  | 5 | - | - |  |  | UV254 Transmission | % T10 | <5 | - | - | Very Poor
Comments: | The sample was |  | slightly discoloured |  | with | no significant sediments |  | Comments: The sample was slightly discoloured with no significant sediments
LSI comment: | The negative LSI indicates corrosive water. | [6 empty] | The negative LSI indicates corrosive water.
Silica comment:
Iron comment:
Manganese comment:
MAV comment:
[8 empty] | GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
[8 empty] | MAV2 | Maximum Acceptable Value - Water Services (Drinking Water Standards for New Zealand) Regulations 2022
[8 empty] | mg/L | = ppm, = g/m3
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## R-SRT
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | Rev12 | LABORATORY WATER ANALYSIS REPORT | [6 empty] | Rev12
Dealer Name | Think Water Gisborne |  |  |  |  | Sample No. | 20240515SRT01 |  | Think Water Gisborne | [5 empty] | Sample No. | 20240515SRT01
Reference Name | Cranswick |  |  |  |  | Date Received | 2024-05-15 |  | Cranswick | [5 empty] | Date Received | 2024-05-15
Sample Type | Ground Water |  |  |  |  | Date Tested | 2024-05-16 |  | Sample Type | Ground Water |  |  |  |  | Date Reported | 2024-05-20
|  | 1 | 2 | 3 | 4 | [6 empty] | 1 | 2 | 3 | 4
Test Parameter | Units / Name: | Raw Flush | Raw 20min | SRT | TSRT |  |  |  | Test Parameter | Units | GV1 | Raw Flush | Raw 20min | SRT | TSRT
pH | - | 7.4 | 7.5 | 7.5 | 7.2 |  |  |  | pH | - | 7.0 - 8.5 | 7.4 | 7.5 | 7.5 | 7.2
Alkalinity | mg/L CaCO3 | 330 | 330 | 320 | 145 |  |  |  | Alkalinity | mg/L CaCO3 | - | 330 | 330 | 320 | 145
Total Hardness | mg/L CaCO3 | 390 | 260 | 15 | 0 |  |  |  | Total Hardness | mg/L CaCO3 | ≤200 | 390 | 260 | 15 | <5
Free Carbon Dioxide | mg/L CO2 | 26.2122 | 20.8082 | 20.1776 | 18.2695 |  |  |  | Free Carbon Dioxide | mg/L CO2 | - | 26.2122 | 20.8082 | 20.1776 | 18.2695
Langelier Saturation | - | 0.4 | 0.4 | -1 | -2 |  |  |  | Langelier Saturation | - | - | 0.4 | 0.4 | -1 | -2
Total Iron | mg/L | 0.11 | 2.75 | 1.6 | 0.23 |  |  |  | Total Iron | mg/L | ≤0.3 | 0.11 | 2.75 | 1.6 | 0.23
Total Manganese | mg/L | 0.14 | 0.3 | <0.01 | <0.01 |  |  |  | Total Manganese | mg/L | ≤0.04 | 0.14 | 0.3 | <0.01 | <0.01
Total Dissolved Solids | mg/L | 480 | 490 | 510 | 580 |  |  |  | Total Dissolved Solids | mg/L | ≤1000 | 480 | 490 | 510 | 580
Chloride | mg/L | 64 | 55 | 53 | 215 |  |  |  | Chloride | mg/L | ≤250 | 64 | 55 | 53 | 215
Sodium | mg/L | 72 | 74 | 250 | 260 |  |  |  | Sodium | mg/L | ≤200 | 72 | 74 | 250 | 260
Conductivity | mS/m | 67.2 | 68.9 | 71.2 | 81.7 |  |  |  | Conductivity | mS/m | - | 67.2 | 68.9 | 71.2 | 81.7
Conductivity | µS/cm | 672 | 689 | 712 | 817 |  |  |  | Conductivity | µS/cm | - | 672 | 689 | 712 | 817
Turbidity | NTU | 1.73 | 31.48 | 9.85 | 0.03 |  |  |  | Turbidity | NTU | ≤5 | 1.73 | 31.48 | 9.85 | <0.05
Colour | °H | <5 | <5 | <5 | <5 |  |  |  | Colour | °H | - | <5 | <5 | <5 | <5
UV254 Transmission | % T10 | 87.8 | 70 | 57.9 | 95.6 |  |  |  | UV254 Transmission | % T10 | - | 87.8 | 70 | 57.9 | 95.6
Comments | [8 empty] | Comments | Samples were taken by Client and tested as received by the laboratory
Sample 1 | The sample was |  | slightly discoloured |  | with | sediments |  |  | Sample 1 | The sample was slightly discoloured with sediments
Sample 2 | The sample was |  | discoloured |  | with | some significant sediments |  |  | Sample 2 | The sample was discoloured with some significant sediments
Sample 3 | The sample was |  | slightly discoloured |  | with | no significant sediments |  |  | Sample 3 | The sample was slightly discoloured with no significant sediments
Sample 4 | The sample was |  | clear |  | with | no significant sediments |  |  | Sample 4 | The sample was clear with no significant sediments
[9 empty] | GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
[9 empty] | mg/L | = ppm, = g/m3
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## R-COM
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | Rev12 | LABORATORY WATER ANALYSIS REPORT | [7 empty] | Rev12
Dealer Name | [5 empty] | Sample No. | 20230202CHM01 |  | DEALER NAME | [5 empty] | Sample No. |  | 20230202CHM01
Reference Name | [5 empty] | Date Received |  |  | REFERENCE NAME | [5 empty] | Date Received |  | 0
Sample Type | TBC |  |  |  |  | Date Tested |  |  | Sample Type | TBC |  |  |  |  | Date Reported |  | 2024-05-20
|  | 1 | 2 | 3 | 4 | 5 | 6 |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Test Parameter | Units / Name: | [7 empty] | Test Parameter | Units | GV1 | 0 | 0 | 0 | 0 | 0 | 0
pH | - | [7 empty] | pH | - | 7.0 - 8.5 | 0 | 0 | 0 | 0 | 0 | 0
Alkalinity | mg/L CaCO3 | [7 empty] | Alkalinity | mg/L CaCO3 | - | <5 | <5 | <5 | <5 | <5 | <5
Total Hardness | mg/L CaCO3 | [7 empty] | Total Hardness | mg/L CaCO3 | ≤200 | <5 | <5 | <5 | <5 | <5 | <5
Calcium Hardness | mg/L CaCO3 | [7 empty] | Calcium Hardness | mg/L CaCO3 | - | <5 | <5 | <5 | <5 | <5 | <5
Magnesium Hardness | mg/L CaCO3 | 0 | 0 | 0 | 0 | 0 | 0 |  | Magnesium Hardness | mg/L CaCO3 | - | <5 | <5 | <5 | <5 | <5 | <5
Free Carbon Dioxide | mg/L CO2 | 9999999.9981 | 9999999.9981 | 9999999.9981 | 9999999.9981 | 9999999.9981 | 9999999.9981 |  | Free Carbon Dioxide | mg/L CO2 | - | 9999999.9981 | 9999999.9981 | 9999999.9981 | 9999999.9981 | 9999999.9981 | 9999999.9981
Langelier Saturation | - | -10.6 | -10.6 | -10.6 | -10.6 | -10.6 | -10.6 |  | Langelier Saturation | - | - | -10.6 | -10.6 | -10.6 | -10.6 | -10.6 | -10.6
Silica | mg/L SiO2 | [7 empty] | Silica | mg/L SiO2 | - | <5 | <5 | <5 | <5 | <5 | <5
Nitrate | mg/L NO3 | [7 empty] | Nitrate | mg/L NO3 | - | <1 | <1 | <1 | <1 | <1 | <1
Sulphate | mg/L SO4 | [7 empty] | Sulphate | mg/L SO4 | ≤250 | <1 | <1 | <1 | <1 | <1 | <1
Total Iron | mg/L | [7 empty] | Total Iron | mg/L | ≤0.3 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01
Total Manganese | mg/L | [7 empty] | Total Manganese | mg/L | ≤0.04 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01
Total Aluminium | mg/L | [7 empty] | Total Aluminium | mg/L | ≤0.1 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01
Total Copper | mg/L | [7 empty] | Total Copper | mg/L | ≤1 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01
Total Dissolved Solids | mg/L | [7 empty] | Total Dissolved Solids | mg/L | ≤1000 | <10 | <10 | <10 | <10 | <10 | <10
Chloride | mg/L | [7 empty] | Chloride | mg/L | ≤250 | <1 | <1 | <1 | <1 | <1 | <1
Sodium | mg/L | [7 empty] | Sodium | mg/L | ≤200 | <1 | <1 | <1 | <1 | <1 | <1
Conductivity | mS/m | [7 empty] | Conductivity | mS/m | - | <5 | <5 | <5 | <5 | <5 | <5
Conductivity | µS/cm | [7 empty] | Conductivity | µS/cm | - | 0 | 0 | 0 | 0 | 0 | 0
Turbidity | NTU | [7 empty] | Turbidity | NTU | ≤5 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05
Colour | °H | [7 empty] | Colour | °H | - | <5 | <5 | <5 | <5 | <5 | <5
UV254 Transmission | % T10 | [7 empty] | UV254 Transmission | % T10 | - | <5 | <5 | <5 | <5 | <5 | <5
Total Coliforms (P/A) | /100mL | [7 empty] | Total Coliforms (P/A) | /100mL | - | - | - | - | - | - | bar: 1 to Date Tested 6
E. coli (P/A) | /100mL | [7 empty] | E. coli (P/A) | /100mL | - | - | - | - | - | - | bar: 1 to Date Tested 6
Total Coliforms (MPN) | MPN/100mL | [7 empty] | Total Coliforms (MPN) | MPN/100mL
E. coli (MPN) | MPN/100mL | [7 empty] | E. coli (MPN) | MPN/100mL
Comments | [8 empty] | Comments | Samples were taken by Client and tested as received by the laboratory
Sample 1 | The sample was | 2: slightly discoloured; 4: with; Date Tested 5: no significant sediments |  | Sample 1 | The sample was slightly discoloured with no significant sediments
Sample 2 | The sample was | 2: slightly discoloured; 4: with; Date Tested 5: no significant sediments |  | Sample 2 | The sample was slightly discoloured with no significant sediments
Sample 3 | The sample was | 2: slightly discoloured; 4: with; Date Tested 5: no significant sediments |  | Sample 3 | The sample was slightly discoloured with no significant sediments
Sample 4 | The sample was | 2: slightly discoloured; 4: with; Date Tested 5: no significant sediments |  | Sample 4 | The sample was slightly discoloured with no significant sediments
Sample 5 | The sample was | 2: slightly discoloured; 4: with; Date Tested 5: no significant sediments |  | Sample 5 | The sample was slightly discoloured with no significant sediments
Sample 6 | The sample was | 2: slightly discoloured; 4: with; Date Tested 5: no significant sediments |  | Sample 6 | The sample was slightly discoloured with no significant sediments
[9 empty] | GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
[9 empty] | mg/L | = ppm, = g/m3
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## R-ECO
LABORATORY WATER ANALYSIS REPORT | [6 empty] | Rev12
DEALER NAME | [5 empty] | Sample No. | 20170714COM01
REFERENCE NAME | [5 empty] | Date Received | 2018-09-11
Sample Type | Ground Water |  |  |  |  | Date Reported | 2024-05-20
Test Parameter | Units | Result | GV1 | MAV2 | Comments
Total Coliforms (P/A) | /100mL | - | - | - | #N/A
E. coli (P/A) | /100mL | - | - | <1 | #N/A
Comments:
Testing did not detect the presence of microorganisms in the sample however a form of treatment is recommended if not already installed.
Testing was carried out using the Colitag™ method.
A more complete analysis can be carried out by an accredited microbiological laboratory if required.
The sample was received outside of the maximum allowable time of 24 hours, which may give an inaccurate result. Re-sampling is recommended.
GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
MAV2 | Maximum Acceptable Value - Water Services (Drinking Water Standards for New Zealand) Regulations 2022
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## R-MPN
LABORATORY WATER ANALYSIS REPORT | [6 empty] | Rev12
DEALER NAME | [5 empty] | Sample No. | 20170714COM01
REFERENCE NAME | [5 empty] | Date Received | 2018-09-11
Sample Type | Ground Water |  |  |  |  | Date Reported | 2024-05-20
Test Parameter | Units | Result | GV1 | MAV2 | Comments
Total Coliforms (MPN) | MPN/100mL |  | - | - | #N/A
E. coli (MPN) | MPN/100mL |  | - | <1.1 | #N/A
Comments:
The sample contained E. coli, which indicates faecal contamination. Drink bottled water or boiled (and cooled) water until treatment is installed
Testing was carried out using the Colitag™ method.
The Most Probable Number (MPN) count uses reference method APHA 9221 C, Table 9221:III
A more complete analysis can be carried out by an accredited microbiological laboratory if required.
The sample was received outside of the maximum allowable time of 24 hours, which may give an inaccurate result. Re-sampling is recommended.
GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
MAV2 | Maximum Acceptable Value - Water Services (Drinking Water Standards for New Zealand) Regulations 2022
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## R-C+E
LABORATORY WATER ANALYSIS - TEST SHEET | [6 empty] | Rev12 | LABORATORY WATER ANALYSIS REPORT | [6 empty] | Rev12
Dealer Name | [5 empty] | Sample No. |  | DEALER NAME | [5 empty] | Sample No. | 0
Reference Name | [5 empty] | Date Received |  | REFERENCE NAME | [5 empty] | Date Received | 0
Sample Type | [5 empty] | Date Tested |  | Sample Type | TBC |  |  |  |  | Date Reported | 2024-05-20
Test Parameter | Units / Name: | Result | DL | GV | MAV | Comment |  | Test Parameter | Units | Result | GV1 | MAV2 | Comments
pH | - |  |  | 7.0 - 8.5 | - |  |  | pH | - | 0 | 7.0 - 8.5 | - | #N/A
Alkalinity | mg/L CaCO3 |  | 5 | - | - |  |  | Alkalinity | mg/L CaCO3 | <5 | - | - | Trace
Total Hardness | mg/L CaCO3 |  | 5 | ≤200 | - |  |  | Total Hardness | mg/L CaCO3 | <5 | ≤200 | - | Trace
Calcium Hardness | mg/L CaCO3 |  | 5 | - | - |  |  | Calcium Hardness | mg/L CaCO3 | <5 | - | - | Trace
Magnesium Hardness | mg/L CaCO3 | 0 | 5 | - | - |  |  | Magnesium Hardness | mg/L CaCO3 | <5 | - | - | Trace | Calculated Result
Free Carbon Dioxide | mg/L CO2 | 9999999.9981 |  | - | - |  |  | Free Carbon Dioxide | mg/L CO2 | 9999999.9981 | - | - | Very High | Calculated Result
Langelier Saturation | - | -10.6 |  | - | - |  |  | Langelier Saturation Index | - | -10.6 | - | - | #N/A | Calculated Result
Silica | mg/L SiO2 |  | 1 | - | - |  |  | Silica | mg/L SiO2 | <5 | - | - | Not Detected
Nitrate | mg/L NO3 |  | 1 | - | 50 |  |  | Nitrate | mg/L NO3 | <1 | - | 50 | Not Detected
Sulphate | mg/L SO4 |  | 1 | ≤250 |  |  |  | Sulphate | mg/L SO4 | <1 | ≤250 | - | Not Detected
Total Iron | mg/L |  | 0.01 | ≤0.3 | - |  |  | Total Iron | mg/L | <0.01 | ≤0.3 | - | Not Detected
Total Manganese | mg/L |  | 1.5 | ≤0.04 | 0.4 |  |  | Total Manganese | mg/L | <0.01 | ≤0.04 | 0.4 | Not Detected | <0.04 Staining, <0.10 Taste
Total Aluminium | mg/L |  | 0.01 | ≤0.1 | - |  |  | Total Aluminium | mg/L | <0.01 | ≤0.1 | - | Not Detected
Total Copper | mg/L |  | 0.01 | ≤1 | 2 |  |  | Total Copper | mg/L | <0.01 | ≤1 | 2 | Not Detected
Total Dissolved Solids | mg/L |  | 10 | ≤1000 | - |  |  | Total Dissolved Solids | mg/L | <10 | ≤1000 | - | Trace | Calculated Result
Chloride | mg/L |  | 1 | ≤250 | - |  |  | Chloride | mg/L | <1 | ≤250 | - | Trace
Sodium | mg/L |  |  | ≤200 | - |  |  | Sodium | mg/L | <1 | ≤200 | - | Trace
Conductivity | mS/m | 0 |  | - | - |  |  | Conductivity | mS/m | 0 | - | - | -
Conductivity | µS/cm |  |  | - | - |  |  | Conductivity | µS/cm | 0 | - | - | -
Turbidity | NTU |  | 0.05 | ≤5 | - |  |  | Turbidity | NTU | <0.05 | ≤5 | - | Very Low | ≤ 5 for Appearance
Colour | °H |  | 5 | - | - |  |  | Colour | °H | <5 | - | - | Very Low | ≤ 15 TCU for Appearance
UV254 Transmission | % T10 |  | 5 | - | - |  |  | UV254 Transmission | % T10 | <5 | - | - | Very Poor
Total Coliforms (P/A) | /100mL |  |  | - | - |  |  | Total Coliforms (P/A) | /100mL |  | - | - | #N/A
E. coli (P/A) | /100mL |  |  | - | - |  |  | E. coli (P/A) | /100mL |  | - | <1 | #N/A
Comments: | The sample was |  | clear |  | with | no significant sediments |  | Comments: The sample was clear with no significant sediments
LSI comment: | The negative LSI indicates corrosive water. | [6 empty] | The negative LSI indicates corrosive water.
Silica comment:
Iron comment:
Manganese comment:
Chloride comment:
E. coli comment: | Testing did not detect the presence of microorganisms in the sample however a form of treatment is recommended if not already installed. | [6 empty] | Testing did not detect the presence of microorganisms in the sample however a form of treatment is recommended if not already installed.
MAV comment:
[8 empty] | GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
[8 empty] | MAV2 | Maximum Acceptable Value - Water Services (Drinking Water Standards for New Zealand) Regulations 2022
[8 empty] | mg/L | = ppm, = g/m3
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## R-C+M
LABORATORY WATER ANALYSIS - TEST SHEET | [6 empty] | Rev12 | LABORATORY WATER ANALYSIS REPORT | [6 empty] | Rev12
Dealer Name | [5 empty] | Sample No. | 20170714C+M01 | DEALER NAME | [5 empty] | Sample No. | 20170714C+M01
Reference Name | [5 empty] | Date Received |  | REFERENCE NAME | [5 empty] | Date Received | 0
Sample Type | TBC |  |  |  |  | Date Tested |  | Sample Type | TBC |  |  |  |  | Date Reported | 2024-05-20
Test Parameter | Units / Name: | Result | DL | GV | MAV | Comment |  | Test Parameter | Units | Result | GV1 | MAV2 | Comments
pH | - |  |  | 7.0 - 8.5 | - |  |  | pH | - | 0 | 7.0 - 8.5 | - | #N/A
Alkalinity | mg/L CaCO3 |  | 5 | - | - |  |  | Alkalinity | mg/L CaCO3 | <5 | - | - | Trace
Total Hardness | mg/L CaCO3 |  | 5 | ≤200 | - |  |  | Total Hardness | mg/L CaCO3 | <5 | ≤200 | - | Trace
Calcium Hardness | mg/L CaCO3 |  | 5 | - | - |  |  | Calcium Hardness | mg/L CaCO3 | <5 | - | - | Trace
Magnesium Hardness | mg/L CaCO3 | 0 | 5 | - | - |  |  | Magnesium Hardness | mg/L CaCO3 | <5 | - | - | Trace | Calculated Result
Free Carbon Dioxide | mg/L CO2 | 9999999.9981 |  | - | - |  |  | Free Carbon Dioxide | mg/L CO2 | 9999999.9981 | - | - | Very High | Calculated Result
Langelier Saturation | - | -10.6 |  | - | - |  |  | Langelier Saturation Index | - | -10.6 | - | - | #N/A | Calculated Result
Silica | mg/L SiO2 |  | 1 | - | - |  |  | Silica | mg/L SiO2 | <5 | - | - | Not Detected
Nitrate | mg/L NO3 |  | 1 | - | 50 |  |  | Nitrate | mg/L NO3 | <1 | - | 50 | Not Detected
Sulphate | mg/L SO4 |  | 1 | ≤250 |  |  |  | Sulphate | mg/L SO4 | <1 | ≤250 | - | Not Detected
Total Iron | mg/L |  | 0.01 | ≤0.3 | - |  |  | Total Iron | mg/L | <0.01 | ≤0.3 | - | Not Detected
Total Manganese | mg/L |  | 1.5 | ≤0.04 | 0.4 |  |  | Total Manganese | mg/L | <0.01 | ≤0.04 | 0.4 | Not Detected | <0.04 Staining, <0.10 Taste
Total Aluminium | mg/L |  | 0.01 | ≤0.1 | - |  |  | Total Aluminium | mg/L | <0.01 | ≤0.1 | - | Not Detected
Total Copper | mg/L |  | 0.01 | ≤1 | 2 |  |  | Total Copper | mg/L | <0.01 | ≤1 | 2 | Not Detected
Total Dissolved Solids | mg/L |  | 10 | ≤1000 | - |  |  | Total Dissolved Solids | mg/L | <10 | ≤1000 | - | Trace | Calculated Result
Chloride | mg/L |  | 1 | ≤250 | - |  |  | Chloride | mg/L | <1 | ≤250 | - | Trace
Sodium | mg/L |  |  | ≤200 | - |  |  | Sodium | mg/L | <1 | ≤200 | - | Trace
Conductivity | mS/m | 0 |  | - | - |  |  | Conductivity | mS/m | 0 | - | - | -
Conductivity | µS/cm |  |  | - | - |  |  | Conductivity | µS/cm | 0 | - | - | -
Turbidity | TCU |  | 0.05 | ≤5 | - |  |  | Turbidity | TCU | <0.05 | ≤5 | - | Very Low | ≤ 5 for Appearance
Colour | °H |  | 5 | - | - |  |  | Colour | °H | <5 | - | - | Very Low | ≤ 15 TCU for Appearance
UV254 Transmission | % T10 |  | 5 | - | - |  |  | UV254 Transmission | % T10 | <5 | - | - | Very Poor
Total Coliforms (MPN) | MPN/100mL | <1.1 |  | - | - |  |  | Total Coliforms (MPN) | MPN/100mL | <1.1 | - | - | Ideal
E. coli (MPN) | MPN/100mL | <1.1 |  | - | - |  |  | E. coli (MPN) | MPN/100mL | <1.1 | - | <1 | Ideal
Comments: | The sample was |  | slightly discoloured |  | with | no significant sediments |  | Comments: The sample was slightly discoloured with no significant sediments
LSI comment: | The negative LSI indicates corrosive water. | [6 empty] | The negative LSI indicates corrosive water.
Silica comment:
Iron comment:
Manganese comment:
Chloride comment:
E. coli comment: | Testing did not detect the presence of microorganisms in the sample however a form of treatment is recommended if not already installed. | [6 empty] | Testing did not detect the presence of microorganisms in the sample however a form of treatment is recommended if not already installed.
MAV comment:
[8 empty] | GV1 | Guideline Value - Aesthetic Values for Drinking Water Notice 2022
[8 empty] | MAV2 | Maximum Acceptable Value - Water Services (Drinking Water Standards for New Zealand) Regulations 2022
[8 empty] | mg/L | = ppm, = g/m3
Jewella Sepulveda
Water Treatment Specialist
Email: nzlab@dwp.co.nz
Whilst care is taken to ensure the accuracy of this information, Davey Water Products does not accept responsibility for any loss or damage based on it.

## T-CHE
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | #REF!
FULL CHEM
Dealer Name | [5 empty] | Sample No.
Reference Name | [5 empty] | Date Received
Sample Type | [5 empty] | Date Tested
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Test Parameter | Units / Name:
pH | -
Alkalinity | mg/L CaCO3
Total Hardness | mg/L CaCO3
Calcium Hardness | mg/L CaCO3
Silica | mg/L SiO2
Nitrate | mg/L NO3
Sulphate | mg/L SO4
Total Iron | mg/L
Total Manganese | mg/L
Total Aluminium | mg/L
Total Copper | mg/L
Total Dissolved Solids | mg/L
Chloride | mg/L
Sodium | mg/L
Conductivity | mS/m µS/cm
Turbidity | NTU
Colour | °H
UV254 Transmission | % T10
Comments
Sample 1 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 2 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 3 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 4 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 5 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 6 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 7 | The sample was clear / slightly discoloured with no / some significant sediment

## T-SHO
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | #REF!
SHORT CHEM
Dealer Name | [5 empty] | Sample No.
Reference Name | [5 empty] | Date Received
Sample Type | [5 empty] | Date Tested
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Test Parameter | Units / Name:
pH | -
Alkalinity | mg/L CaCO3
Total Hardness | mg/L CaCO3
Silica | mg/L SiO2
Total Iron | mg/L
Total Manganese | mg/L
Total Dissolved Solids | mg/L
Turbidity | NTU
UV254 Transmission | % T10
Comments
Sample 1 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 2 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 3 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 4 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 5 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 6 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 7 | The sample was clear/slightly discoloured with no/some significant sediment

## T-SRT
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | #REF!
SRT
Dealer Name | [5 empty] | Sample No.
Reference Name | [5 empty] | Date Received
Sample Type | [5 empty] | Date Tested
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Test Parameter | Units / Name: | Raw Flush | Raw 20min | SRT | TSRT | 5µm Filtered | 5µm SRT | 5µm TSRT
pH | -
Alkalinity | mg/L CaCO3
Total Hardness | mg/L CaCO3
Total Iron | mg/L
Total Manganese | mg/L
Total Dissolved Solids | mg/L
Chloride | mg/L
Sodium | mg/L
Conductivity | mS/m µS/cm
Turbidity | NTU
Colour | °H
UV254 Transmission | % T10
Comments
Sample 1 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 2 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 3 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 4 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 5 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 6 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 7 | The sample was clear/slightly discoloured with no/some significant sediment

## T-ECO
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | #REF!
MICRO
Dealer Name | [5 empty] | Sample No.
Reference Name | [5 empty] | Date Received
Sample Type | [5 empty] | Date Tested
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Test Parameter | Units / Name:
Total Coliforms (P/A) | /100mL
E. coli (P/A) | /100mL
Total Coliforms (MPN) | MPN/100mL
E. coli (MPN) | MPN/100mL
Comments
Sample 1
Sample 2
Sample 3
Sample 4
Sample 5
Sample 6
Sample 7

## T-TWN
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | #REF!
MUNICIPAL/TOWN SUPPLY
Dealer Name | [5 empty] | Sample No.
Reference Name | [5 empty] | Date Received
Sample Type | Town Supply |  |  |  |  | Date Tested
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Test Parameter | Units / Name:
pH | -
Alkalinity | mg/L CaCO3
Total Hardness | mg/L CaCO3
Silica | mg/L SiO2
Total Iron | mg/L
Total Manganese | mg/L
Total Aluminium | mg/L
Total Dissolved Solids | mg/L
Chloride | mg/L
Conductivity | mS/m µS/cm
Turbidity | NTU
Colour | °H
UV254 Transmission | % T10
Free Available Chlorine | mg/L
Comments
Sample 1 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 2 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 3 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 4 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 5 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 6 | The sample was clear/slightly discoloured with no/some significant sediment
Sample 7 | The sample was clear/slightly discoloured with no/some significant sediment

## T-ALL
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | #REF!
Dealer Name | [5 empty] | Sample No.
Reference Name | [5 empty] | Date Received
Sample Type | [5 empty] | Date Tested
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Test Parameter | Units / Name:
pH | -
Alkalinity | mg/L CaCO3
Total Hardness | mg/L CaCO3
Calcium Hardness | mg/L CaCO3
Magnesium Hardness | mg/L CaCO3
Free Carbon Dioxide | mg/L CO2
Langelier Saturation | -
Silica | mg/L SiO2
Nitrate | mg/L NO3
Total Iron | mg/L
Total Manganese | mg/L
Total Aluminium | mg/L
Total Copper | mg/L
Total Dissolved Solids | mg/L
Chloride | mg/L
Sodium | mg/L
Conductivity | mS/m
Conductivity | µS/cm
Turbidity | NTU
Colour | °H
UV254 Transmission | % T10
Free Available Chlorine | mg/L
Combined Chlorine | mg/L
Total Chlorine | mg/L
Total Coliforms (P/A) | /100mL
E. coli (P/A) | /100mL
Total Coliforms (MPN) | MPN/100mL
E. coli (MPN) | MPN/100mL
Comments
Sample 1 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 2 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 3 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 4 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 5 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 6 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 7 | The sample was clear / slightly discoloured with no / some significant sediment

## Data
Form Data
XXXXXX
P/A
-
Present
<1
MDL
0.01 | <0.01 | Total Iron
Total Manganese
Total Aluminium
Total Copper
0.05 | <0.05 | Turbidity
0.1 | <0.10 | Total Chlorine
Free Available Chlorine
1 | <1 | Silica
Chloride
Sodium
1.1 | <1.1 | Total Coliforms (MPN)
E. coli (MPN)
5 | <5 | Alkalinity
Total Hardness
Calcium Hardness
Magnesium Hardness
Free Carbon Dioxide
Total Dissolved Solids
UV254 Transmission
Sample Type
TBC
Ground Water
Surface Water
Rain Water
Waste Water
Salt Water
Process Water
Town Supply
Blended Source
Micro comment
Testing did not detect the presence of microorganisms in the sample however a form of treatment is recommended if not already installed.
The presence of microorganisms in the sample indicates a significant health risk. Treatment is highly recommended.
The sample contained E. coli, which indicates faecal contamination. Drink bottled water or boiled (and cooled) water until treatment is installed
MPN | Count
<1.1 | 0
1.1 | 1
2.2 | 2
3.6 | 3
5.1 | 4
6.9 | 5
9.2 | 6
12 | 7
16 | 8
23 | 9
>23 | 10

## Lookup
Lookup
PH:
| 1 | Very Acidic
| 5.5 | Very Acidic
| 5.7 | Acidic
| 7 | Neutral
| 8.1 | Alkaline
TDS:
| <10 | Trace
| 10 | Low
| 99 | Low
| 100 | Moderate
| 299 | Moderate
| 300 | High
| 499 | High
| 999 | Excessive
Alkalinity:
| <5 | Trace
| 5 | Low
| 49 | Low
| 50 | Moderate
| 149 | Moderate
| 150 | High
| 299 | High
| 300 | Excessive
Total Hardness:
| <5 | Trace
| 5 | Soft
| 20 | Slightly Hard
| 60 | Moderate
| 120 | Hard
| 180 | Very Hard
| 300 | Excessive
Calcium & Magnesium:
| <5 | Trace
| 5 | Soft
| 20 | Slightly Hard
| 60 | Moderate
| 120 | Hard
| 180 | Very Hard
| 300 | Excessive
Silica:
| <5 | Not Detected
| 5 | Low
| 15 | Low
| 16 | Moderate
| 49 | Moderate
| 50 | Significant
| 89 | Significant
| 90 | High
Iron:
| <0.01 | Not Detected
| 0.01 | Low
| 0.1 | Moderate
| 0.2 | Significant
| 1 | High
| 5 | Very High
| 10 | Excessive
| 12.1 | Excessive
Manganese:
| <0.01 | Not Detected
| 0.01 | Low
| 0.04 | High
| 0.1 | Very High
| 0.4 | Above MAV
Aluminium:
| <0.01 | Not Detected
| 0.01 | Low
| 0.09 | Low
| 0.1 | Significant
| 0.2 | High
| 0.3 | Very High
Copper:
| <0.01 | Not Detected
| 0.01 | Low
| 0.2 | Elevated
| 1 | High
| 2 | Above MAV
Sodium/Chloride:
| <1 | Trace
| 1 | Low
| 10 | Low
| 50 | Moderate
| 150 | Significant
| 200 | High
| 350 | Very High
| 500 | Excessive
Nitrate:
| <1 | Not Detected
| 1 | Low
| 9 | Low
| 10 | Elevated
| 20 | Significant
| 30 | High
| 40 | Very High
| 50 | Above MAV
Free Carbon Dioxide:
| <1 | Trace
| 1 | Low
| 9 | Low
| 10 | Significant
| 40 | High
| 50 | Very High
Langelier Index:
| -10 | Aggressive
| -2 | Corrosive
| -1 | Normal
| 1 | Scale Forming
| 2 | Scale Forming
T.coli P/A: | Present | Warning
| <1 | Ideal
E.coli P/A: | Present | ALERT
| <1 | Ideal
T.coli MPN: | <1.1 | Ideal
| >23 | Warning
| 1.1 | Warning
| 24 | Warning
E.coli MPN: | <1.1 | Ideal
| >23 | ALERT
| 1.1 | ALERT
| 24 | ALERT
Turbidity
| <0.05 | Very Low
| 0.05 | Very Low
| 0.3 | Low
| 1 | Elevated
| 2.5 | Significant
| 5 | High
| 20 | Very High
| 40 | Excessive
UVT
| <5 | Very Poor
| 5 | Very Poor
| 75 | Poor
| 80 | Below Ideal
| 85 | Moderate
| 90 | Good
| 95 | Very Good
FAC
| <0.01 | Not Detected
| 0.01 | Very Low
| 0.2 | Low
| 0.6 | Ideal
| 1.1 | High
| 2 | Very High
| 5 | Above MAV
Colour
| <5 | Very Low
| 5 | Low
| 30 | Moderate
| 50 | High
Sulphate:
| <1 | Not Detected
| 1 | Low
| 50 | Low
| 75 | Moderate
| 100 | Moderate
| 200 | Significant
| 250 | High

## LSI
1 |  |  |  | CF | AF |  | LSI
| Results | Factors | 5 | 0.3 | 5 | 0.7 | -3 | Corrosive
PH | #REF! |  | 7.8571 | 0.4 | 7.8571 | 0.8 | -0.6 | Corrosive
Total Hardness | #REF! | #REF! | 10.7143 | 0.5 | 10.7143 | 0.9 | -0.5 | Acceptable
Alkalinity | #REF! | #REF! | 13.5714 | 0.6 | 13.5714 | 1 | 0.5 | Acceptable
LSI | #REF! |  | 16.4286 | 0.7 | 16.4286 | 1.1 | 0.6 | Scale forming
| #REF! |  | 19.2857 | 0.8 | 19.2857 | 1.2
|  |  | 22.1429 | 0.9 | 22.1429 | 1.3
|  |  | 25 | 1 | 25 | 1.4
|  |  | 33.3333 | 1.1 | 33.33 | 1.5
|  |  | 41.6667 | 1.2 | 41.66 | 1.6
|  |  | 50 | 1.3 | 50 | 1.7
|  |  | 62.5 | 1.4 | 62.5 | 1.8
|  |  | 75 | 1.5 | 75 | 1.9
|  |  | 100 | 1.6 | 100 | 2
|  |  | 125 | 1.7 | 125 | 2.1
|  |  | 150 | 1.8 | 150 | 2.2
|  |  | 200 | 1.9 | 200 | 2.3
|  |  | 250 | 2 | 250 | 2.4
|  |  | 300 | 2.1 | 300 | 2.5
|  |  | 400 | 2.2 | 400 | 2.6
|  |  | 533.3333 | 2.3 | 533.33 | 2.7
|  |  | 666.6667 | 2.4 | 666.66 | 2.8
|  |  | 800 | 2.5 | 800 | 2.9
|  |  | 1000 | 2.6 | 1000 | 3

## Input sheet
LABORATORY WATER ANALYSIS - TEST SHEET | [7 empty] | #REF!
Dealer Name | [5 empty] | Sample No.
Reference Name | [5 empty] | Date Received
Sample Type | [5 empty] | Date Tested
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7
Test Parameter | Units / Name:
pH | -
Alkalinity | mg/L CaCO3
Total Hardness | mg/L CaCO3
Calcium Hardness | mg/L CaCO3
Magnesium Hardness | mg/L CaCO3
Free Carbon Dioxide | mg/L CO2
Langelier Saturation | -
Silica | mg/L SiO2
Nitrate | mg/L NO3
Total Iron | mg/L
Total Manganese | mg/L
Total Aluminium | mg/L
Total Copper | mg/L
Total Dissolved Solids | mg/L
Chloride | mg/L
Sodium | mg/L
Conductivity | mS/m
Conductivity | µS/cm
Turbidity | NTU
Colour | °H
UV254 Transmission | % T10
Free Available Chlorine | mg/L
Combined Chlorine | mg/L
Total Chlorine | mg/L
Total Coliforms (P/A) | /100mL
E. coli (P/A) | /100mL
Total Coliforms (MPN) | MPN/100mL
E. coli (MPN) | MPN/100mL
Comments
Sample 1 | The sample was | 2: slightly discoloured; 4: with; Date Tested 5: some significant sediments | The sample was slightly discoloured with some significant sediments
Sample 2 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 3 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 4 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 5 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 6 | The sample was clear / slightly discoloured with no / some significant sediment
Sample 7 | The sample was clear / slightly discoloured with no / some significant sediment

## Input Lookup sheet
Dealers:
Clarity:
clear
slightly discoloured
discoloured
Sediments
no significant sediments
some significant sediments
sediments